## Slide 1: Tier1 Site Report
HEPSysMan, RAL
10-11 June 2010
Martin Bly, STFC-RAL

## Slide 2: Overview
RAL Stuff
Building stuff
Tier1 Stuff

## Slide 3: STFC Developments
Shared Services Centre
  Provides common services to all the Research Councils:
    HR, Payroll, Procurement, Appraisal ...
  Aim is to provide savings over ‘doing it ourselves’ and by adopting common standards
STFC HR, payroll, procurement now running via SSC
  Mostly positive experience for procurement
  Program underway to look at ‘IT’ procurement needs and processes
    Science computing difficult to fit into this model
  Framework agreements being set up
    Speedier procurement of small batches
    Wider selection types of IT kit available – not just servers
    But may limit choice
    Need to track competitiveness against outsiders
  Do other sites use frameworks and is it a benefit?

## Slide 4: RAL Site
Plan to remove support for old-style f.blogs@rl.ac.uk email addresses in favour of the cross-site standard fred.bloggs@stfc.ac.uk - still under discussion
  significant resistance to this
  no date as yet
International Space Innovation Centre
  “A new environment where government, universities and industry can work together to better exploit scientific opportunities and create new technologies, applications and IP that exploits UK, European and Global Space Programmes”
Will focus on three key areas initially:
  Understanding and countering Climate Change
  Ensuring the Security of space systems and services
  Exploiting the data generated by Earth Observation satellites
Notes: Other Campus developments?

## Slide 5: Building Stuff
UPS problems
  Leading power factor due to switch-mode PSUs in systems
  Causes 3KHz ringing on current, all phases
    Load is small (80kW) compared to capacity of UPS (480kVA).
  Most kit stable but EMC AX4-5 FC arrays unpredictably detect supply failure and shut down arrays
  Longer feed cable from UPS to PDU has made 50% reduction in distortion
  Proposed long-term solution: isolation transformer
New chillers + pumps
  Additional 1500kW cooling capacity: 4 chillers in 3+1 redundant configuration to provide at total of 2250kW
  Additional and replacement higher capacity pumps fitted
Dust in machine rooms

## Slide 7: FY 09/10 Procurements
98 x SuperMicro 4U/24-bay chassis with 2TB SATA HDD
  RAID6 (40TB) or RAID6+1 (38TB) on Adaptec or LSI controllers
  ~3.8PB useable, Site => ~8PB
21 x SuperMicro Twin², 2 x E5520, 3GB/core, 1T HDD
21 x HP SL6000 4-up chassis, 2 x E5520, 3GB/core, 1T HDD
  ~15,500 HS06, Site => ~49,700 HS06, ~5260 cores
FC storage arrays: 7 x Infortrend
iSCSI arrays: 2 x Infortrend
40+ Dell R410 servers
  Tape servers, virtualisation and services hosts
5 HP DL360 database servers with FC
Notes: Usual litany of hardware updates.

## Slide 8: Networking
Additional Force10 C300
  Twin for existing C300
  ‘Spares’, testing
  To be configured as a resilient routing pair
WAN developments
  Existing 10Gb/s site link to SuperJanet5 being doubled to 20Gb/s
    Failover capacity maintained
  LHCOPN failover link @ 10Gb/s
  Both being commissioned
LAN developments
  RAL campus network-futures plan in development

## Slide 10: Storage Commissioning I
One of two batches of the FY08/09 capacity storage failed acceptance testing: 60/110 servers (~1.2PB)
  Rapid onset of failure mode
Supplier involved
  Significant testing with various ‘solutions’ unsuccessful
  Escalated to HDD OEM
  Additional testing program started
    HDD FW variants
  Unable to identify cause of problems
Supplier/OEM agree swap out of disks
  Combination clearly doesn’t work despite compatibility list!

## Slide 11: Storage Commissioning II
One of two batches of FY09/10 capacity storage delayed in proving tests: 60/98 servers (~2.3PB)
  Multiple drive throws
  Disks tested show now issues
Supplier and OEMs involved
New firmware for both controllers and drives
  Flash in-situ
Successful proving test
Now in acceptance testing

## Slide 12: Drive Failure Rates
Chart: Failure Rate Normalised by Installed Base 2009-10
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr
Clustervision 05 | 0.012397 | 0.0020661 | 0.0061983 | 0.0020661 | 0.0082645 | 0.0061983 | 0.012397 | 0.0020661 | 0.02686 | 0.014463 | 0.024793 | 0.018595 | 0 | 0 | 0 | 0
Viglen 06 | 0.01495 | 0.013289 | 0.01412 | 0.017442 | 0.010797 | 0.011628 | 0.024917 | 0.025748 | 0.010797 | 0.023256 | 0.015781 | 0.013289 | 0.011628 | 0.013289 | 0.0049834 | 0.0024917
Viglen 07a | 0.0023548 | 0.0031397 | 0.0031397 | 0.00078493 | 0.0047096 | 0.0047096 | 0.0047096 | 0.0078493 | 0.0023548 | 0.00078493 | 0 | 0.0015699 | 0.0023548 | 0.0031397 | 0.0031397 | 0.0039246
Viglen 07i | 0.0015699 | 0.0039246 | 0.0023548 | 0.0015699 | 0.0047096 | 0.0039246 | 0.0039246 | 0.0047096 | 0.0039246 | 0.0031397 | 0.0023548 | 0.0031397 | 0.0023548 | 0.0047096 | 0.00078493 | 0.00078493
Streamline 08 | 0.0027273 | 0.00090909 | 0.0054545 | 0 | 0 | 0 | 0.0018182 | 0.00090909 | 0 | 0

## Slide 13: Benchmarks
Chart: HS06 Scores - RAL Worker Nodes
| 270 | E5130 | E5410 | L5420 | E5420 | E5440 | E5520
SL4.7/x86_64 | 26.3 | 29.1467 | 62.2633 | 65.11 | 69.0533
SL5.4/x86_64 | 30.9393 | 66.5517 | 69.805 | 70.5053 | 74.6487 | 92.5093

## Slide 14: Fabric Management
Deployment with QUATTOR
Already Deployed:
Worker nodes, Batch server, UK-BDII, LHCb VO box
In Progress now:
Disk Servers, CEs, LFC, Local BDII
Plan:
All system types Quattorised by December 2010
Final catch up rollout during end of year stop

## Slide 15: Grid Services
SL4 to SL5 migration for batch workers
FroNTier deployment
LFC cleanup
FTS upgrade (to version 2.2.3)
glexec deployment, SCAS/pilot roles in progress.
Updates to hardware used for Top-BDII quintet.
Other improvements in resilience e.g. enabling hot-swappable disks on WMS…

## Slide 16: Castor
Done:
  Nameserver upgrade to 2.1.8-3 (September)
  SRM update to 2.8-1 (October)
  Database disk array problem and subsequent rewinding of database. (October)
  Oracle database quarterly patching (November)
  Move back to original disk arrays (January)
  Update memory in database nodes (February)
To come:
  New database architecture and hardware
  Updates to Castor (2.1.8/2.1.9)

## Slide 17: Questions?